Water Treatment Lesson

- Policy

  - Chemical treatment of water is required to maintain the correct pH or chemical balance for use in boilers, heaters, or as an ingredient.

  - Treatment is controlled and carefully monitored where the above are required.

  - Any water used in the manufacturing or sanitation process is verified as potable.

  - Water and boiler (water heater) treatment chemicals are approved for such use and properly stored.

  - There are established methods, responsibilities, and frequencies to monitor the Microbiology and Quality of the water provided by the ENTER CITY NAME, ENTER STATE/COUNTRY ensure its compliance and potability when compared against local and national standards for drinking water.

  - The water supply is sufficient for the operations intended and shall be derived from an adequate source (ENTER CITY NAME).

  - Running water shall be available at a suitable temperature and volume where it is needed for packing, cleaning, sanitation, and employee hygiene.

- Procedures

  - Water Treatment

    - Chlorination- Where in-plant chlorination of water is required for washing, rinsing, or cleaning purposes, a free residual chlorine level of 0.25 ppm after 20 minutes of contact time (or equivalent at the point of use) is recommended. In-line chlorination that provides higher levels of free residual chlorine at specific points is also acceptable. Regular sampling and testing of residual chlorine are implemented to ensure a safe water supply.

    - Reverse osmosis- During this process, a semi-permeable membrane is used to remove ions and unwanted particles. This process can remove both chemicals and bacteria, resulting in potable water safe for food and beverage production.

    - Ion exchange- during ion exchange (IE) treatment, unwanted contaminants are removed from the water and replaced with a non-harmful substance. Ions can be positive or negative, and the replacement substance must have the same type of electrical charge. Keep in mind that ion exchange is a broad treatment and can remove numerous contaminants — including beneficial ones.

    - Carbon filtration- activated carbon filters can reduce organic compounds and chemicals found in drinking water. It can dissolve radon, minimize the quantity of lead, and remove solvents, pesticides, and industrial wastes. It’s crucial to note that activated carbon filtration does not remove metals, nitrates, or microbial contaminants.

    - Settling system uses a tank to remove suspended particles from water. These particles, which have a higher density than the water, fall to the bottom of the tank. Common contaminants removed through settling include fats and greases, hair, sand, grit, wood, bottles, and sludge.

    - UV disinfection- UV (ultraviolet) rays, though invisible to the naked eye, come from the sun and are an effective water treatment option because of its germicidal properties. It can disinfect water from bacteria, viruses, and even protozoans. UV light has been used to purify drinking water in the US as well as commercially in the pharmaceutical, cosmetic, beverage, and electronics industries.

  - Water Testing

    - As a minimum, request testing for biological hazards such as coliforms and E. coli. There should be no E. coli detected in your sample submitted. A test for enteroviruses and fecal indicators may be an option. For example, Salmonella spp, Shigella spp, enterovirulent Vibrio cholera, Yersinia enterocolitica, Campylobacter jejuni, and protozoa.

    - Request Lab tests and analyses conducted by the ENTER CITY NAME every year and review them for compliance. The lab results shall be maintained on file.

    - Conduct a verification lab test once a year of one sample collected inside the plant where the water is utilized for various purposes and conduct the microbiology and Physicochemical lab tests from an authorized lab. The results will be verified and maintained on file. The frequency of analysis has been implemented based on risk.

    - Any water that is used in the operation that could come in contact with the product or for personnel hygiene purposes is verified to be in compliance with local and national standards.

    - In the US and Australia, for example, the potability standard for drinking water is <1 coliform / 100 mL water and membrane filtration is the preferred method. However, standards also apply for Salmonella spp, Shigella spp, enterovirulent E. coli, Vibrio cholera, Yersinia enterocolitica, Campylobacter jejuni, and protozoa.

    - The cleanliness of the water supply is verified bi-annually or annually.

- Responsibility

  - All Personnel

    - Adhere to this policy

  - Preventive Control Qualified Individual (PCQI)

    - Visually inspect areas for compliance with this policy.

    - Oversee (Verify) compliance of procedure.

    - Ensure personnel is trained on this policy and procedures.

    - Monitor and take corrective action to ensure compliance with this policy.

  - Supervisors or Department Heads and Team Leaders

    - Ensure (inspect) and verify this policy and procedure is adhered to and;

    - Take corrective action to ensure compliance with this policy.

- Corrective Action

  - Isolate appropriate water outlets/tanks until satisfactory microbiological test results are obtained

  - Stop production where no potable supply can be provided

  - Review sampling and testing procedures

  - Improve staff instructions and training

  - In the event the city water is deemed to be contaminated, the site will request delivery of potable city water in a tanker from a different city.

- Review – Quality

  - Annual review of water treatment procedures.

  - Annual review of records and interviews with operating personnel. Evidence includes:

    - Water treatment is performed as per written instructions

    - Water treatment that is carried out is appropriate

    - Water treatment is carried out using approved chemicals

    - Water treatment equipment is regularly monitored

    - Treated water is regularly monitored

- History

| Revision No.: | Revision Date: | Description of Change: | Originator / Author Name: | Title / Department: |
| --- | --- | --- | --- | --- |
| 0 | YYYYMMDD | Original | ENTER AUTHOR NAME | ENTER TITLE / ENTER DEPARTMENT |

Requirements:

- The trainee (employee/visitor) has read or received a verbal translation of all or part of the policy, procedure, method, and/or SOP for which they are being trained.

- The trainee has observed a demonstration of the task they are to perform or the procedure for which they are being trained as required.

- The trainee has demonstrated the ability to perform the task with acceptable proficiency and minimal supervision.

| TRAINEE (Print Name): | TRAINEE (Signature): | Date: | Department: |
| --- | --- | --- | --- |
| Trainer / Supervisor (Print Name): | Trainer (Signature): | Date: | Department: |

*Should you need assistance in customizing this document please email services@consultareinc.com